## WF1
Water Site 2.2
PLC Input /Output Point Listing
Rockwell CompactLogix Platform
P&ID Sht # | P&ID Sht Rev # | I/O Status (New or Existing) | I/O Group |  |  | Signal Tag | Device Loop # | Serialized Key | Service Description | I/O Type | Terminal Block Designation #1 | Terminal Block Designation #2 | I/O or Register Address | Signal Origin (Source or Sink) | Signal/ Contact Config (N.O. / N.C. / 4-20mA, etc.) | Signal Voltage | Eng Units (Low/0%) | Eng Units (High/100%) | Eng Units | Alarm Setpoint | Alarm Priority | Pre-FAT Contractor | FAT Programmer | FAT Engineer | FAT Contractor | Pre-Startup Contractor | Startup Programmer | Startup Engineer | Pre-FAT Date | Factory Test Date | Pre-Startup Test Date | Startup Test Date | Pass / Fail | Notes/Comments |  | CONNECTED DI | CONNECTED DO | CONNECTED AI | CONNECTED AO | SPARE DI | SPARE DO | SPARE AI | SPARE AO
|  |  | RACK | SLOT | POINT |  |  |  | I/O Module Type ( CPU ) = 1769-L24ER-QBFC1B | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | New | 1 | 0 | N/A | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | RACK | SLOT | POINT |  |  |  | I/O Type (Embeded Digital Input) | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 0 | JAL-135 |  |  | RTU/Control Section Power Supply Failure | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | RTU/Control Section Power Supply Failure (JAL-135) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 1 | JAL-140 |  |  | RTU/Control Section UPS Alarm | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | RTU/Control Section UPS Alarm (JAL-140) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 2 | EAL-150 |  |  | RTU Section 120VAC Power Failure | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | RTU Section 120VAC Power Failure (EAL-150) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 3 | ZI-100 |  |  | Well In Auto | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | Well In Auto (ZI-100) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 4 | YI-100 |  |  | Well Running | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | Well Running (YI-100) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 5 | UA-100 |  |  | Well Failure Alarm | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | Well Failure Alarm (UA-100) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 6 | PAH-100 |  |  | High Pressure Alarm | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | High Pressure Alarm (PAH-100) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 7 | UA-145 |  |  | SPD Failure | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | SPD Failure (UA-145) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 8 | YI-152 |  |  | MCC Intrusion Alarm | DI |  |  |  |  | N.C. | 24VDC | 0 | 1 | N/A | [15 empty] | MCC Intrusion Alarm (YI-152) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 9 | YI-153 |  |  | Gate Intrusion Alarm | DI |  |  |  |  | N.C. | 24VDC | 0 | 1 | N/A | [15 empty] | Gate Intrusion Alarm (YI-153) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-- | 0 | New | 1 | 1 | 10 | SPARE |  |  | <SPARE> | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
-- | 0 | New | 1 | 1 | 11 | SPARE |  |  | <SPARE> | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
-- | 0 | New | 1 | 1 | 12 | SPARE |  |  | <SPARE> | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
-- | 0 | New | 1 | 1 | 13 | SPARE |  |  | <SPARE> | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
-- | 0 | New | 1 | 1 | 14 | SPARE |  |  | <SPARE> | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
-- | 0 | New | 1 | 1 | 15 | SPARE |  |  | <SPARE> | DI |  |  |  |  | N.O. | 24VDC | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  |  | RACK | SLOT | POINT |  |  |  | I/O Type (Embeded Digital Output) | [25 empty] | I/O Type (Embeded Digital Output) () | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 0 | HS-100A |  |  | Well Start/Stop Command | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | Well Start/Stop Command (HS-100A) | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 1 | 1 | HS-100B |  |  | Well Remote Reset | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | Well Remote Reset (HS-100B) | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
-- | 0 | New | 1 | 1 | 2 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 3 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 4 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 5 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 6 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 7 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 8 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 9 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 10 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 11 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 12 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 13 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 14 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-- | 0 | New | 1 | 1 | 15 | SPARE |  |  | <SPARE> | DO |  |  |  |  | N.O. | -- | 0 | 1 | N/A | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
|  |  | RACK | SLOT | POINT |  |  |  | I/O Type (Embeded Analog Input) | [25 empty] | I/O Type (Embeded Analog Input) () | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 2 | 0 | VIR-140 |  |  | RTU/Control Section Battery Voltage | AI |  |  |  |  | 4-20mA | 24VDC | 0 | 200 | °F | [15 empty] | RTU/Control Section Battery Voltage (VIR-140) | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 2 | 1 | LIR-101 |  |  | Well Level (Submersible) | AI |  |  |  |  | 4-20mA | 24VDC | 0 | 500 | Feet | [15 empty] | Well Level (Submersible) (LIR-101) | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
-- | 0 | New | 1 | 2 | 2 | SPARE |  |  | <SPARE> | AI |  |  |  |  | 4-20mA | 24VDC | 0 | 150 | % | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
-- | 0 | New | 1 | 2 | 3 | SPARE |  |  | <SPARE> | AI |  |  |  |  | 4-20mA | 24VDC | 0 | 100 | % | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
|  |  | RACK | SLOT | POINT |  |  |  | I/O Type (Embeded Analog Input) | [25 empty] | I/O Type (Embeded Analog Input) () | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
I2 | 0 | New | 1 | 2 | 0 | SPARE |  |  | <SPARE> | AO |  |  |  |  | 4-20mA | 24VDC | 0 | 100 | % | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
I2 | 0 | New | 1 | 2 | 1 | SPARE |  |  | <SPARE> | AO |  |  |  |  | 4-20mA | 24VDC | 0 | 100 | % | [15 empty] | <SPARE> (SPARE) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
|  |  | RACK | SLOT | POINT |  |  |  | I/O Type (End Cap) = ECR | [25 empty] | I/O Type (End Cap) = ECR () | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[36 empty] | 10 | 2 | 2 | 0 | 6 | 14 | 2 | 2
[16 empty] | DI/AC | DO | AI | AO
[10 empty] | Connected | [5 empty] | 10 | 2 | 2 | 0
[10 empty] | Spares | [5 empty] | 6 | 14 | 2 | 2
[10 empty] | Total | [5 empty] | 16 | 16 | 4 | 2
[10 empty] | % Spares | [5 empty] | 38% | 87.5% | 50% | 100%